## Residential Load Calculation
LOAD CALCULATIONS - ALTERNATIVE METHOD PER CEC 220.82 | [6 empty] | VA (Watts) |  | Example Appliances: | Check Manufacturer Specifications for Accurate Power Usage
General Lighting & Receptacle Loads |  |  | CEC 220.82(B) | [5 empty] | Appliance | Typical Load VA (Watt)
|  |  | Enter the square foot of your home excluding the garage. | [5 empty] | HVAC
1 | General Lighting |  |  | sq.ft. x | 3 | VA = | 0 |  | Central AC/Heat Pump | 5400 | 1800 | /ton | 3 | tons
Small Appliance & Laundry Loads | [8 empty] | Central Furnace | 1200
2 | 2 small appliance circuits |  | 2 | x | 1500 | VA= | 3000 |  | Air Handler | 1000
3 | Additional small appliance |  | 0 | x | 1500 | VA= | 0
4 | Min. 1 laundry circuit |  | 1 | x | 1500 | VA= | 1500 |  | Water heaters
5 | Dryer | [5 empty] | 5000 |  | Gas - Tank or Tankless | 0
| Range | [5 empty] | 12000 |  | Electric
| Cooktop | [5 empty] | 0 |  | --Tank (Heat Pump) | 4500
| Oven | [5 empty] | 0 |  | --Tankless | Check Product Specifications
| Water Heater | [5 empty] | 4500
| Refrigerator | [5 empty] | 1800 |  | Laundry
| Dishwasher | [5 empty] | 1200 |  | Electric Clothes Dryer | 5000
| Disposal | [5 empty] | 720
| Microwave | [5 empty] | 1800 |  | Kitchen
| EV Charger |  |  | 0 | x1.25 | = | 0 |  | Electric Cooktop | 10800
| Misc | [5 empty] | 0 |  | Electric Single Oven | 4800
| Subtotal | [5 empty] | 31520 |  | Electric Double Oven | 9000
6 | First 10000 VA @ 100% | [5 empty] | 10000 |  | Electric Range | 12000
7 | Balance @ 40% | Balance=(Row 5- Row 6)= |  |  | 21520 | x0.4= | 8608 |  | Built-in Microwave | 1800
| Subtotal | [5 empty] | 18608 |  | Refridgerator | 1800
Special Appliance Loads | [8 empty] | Disposal | 720
8 | AC/Heating @ 100% | [5 empty] | 3600 |  | Dishwasher | 1200
9 | Heat pump + Supplemental Electrical Heating |  |  |  | 0 | x0.65 | 0 |  | Trash Compactor | 1800
10 | Electric Wall Heaters
| Total | [5 empty] | 22208 |  | EV Charger
[8 empty] | VA | 50 Amp | 12000
| TOTAL LOAD= | [5 empty] | 22208 | Amps | 40 Amp | 9600
| Service AMPS = TOTAL LOAD/ 240 V | [5 empty] | 92.5333 | Amps
| Minimum Panel Size (75°C terminals) | [5 empty] | 100 | AWG
| Feeder Conductor Size |  |  |  | Copper |  | 4 | AWG | Feeder/Service Conductor Sizing (CEC Table 310.12) |  |  |  | Grounding Electrode (CEC Table 250.66)
| Grounding Size |  |  |  | Copper |  | 8 |  | Service/Feeder Rating | Conductor Size (AWG or kcmil)
[10 empty] | Copper | Alu or Cu-Clad Alu |  | Copper | Alu or Cu-Clad Alu
[9 empty] | 100 | 4 | 2 |  | 8 | 6
[9 empty] | 110 | 3 | 1
[9 empty] | 125 | 2 | 1/0
[9 empty] | 150 | 1 | 2/0 |  | 6 | 4
[9 empty] | 175 | 1/0 | 3/0
[9 empty] | 200 | 2/0 | 4/0 |  | 4 | 2
[9 empty] | 225 | 3/0 | 250
[9 empty] | 250 | 4/0 | 300 |  | 2 | 1/0
[9 empty] | 300 | 250 | 350
[9 empty] | 350 | 350 | 500
[9 empty] | 400 | 400 | 600 |  | 1/0 | 3/0
Note on P6: 1 ton = 12k BTU 2-4 rooms - 3 tons typ. 1.5 tons minimum
Note on N20: 45A*240V = 10800
Note on N21: 20A * 240V = 4800
Note on B23: CEC 220.80(B)
Note on N23: 50A x 240V = 12,000VA
Note on N24: 15Ax120V = 1800 max
Note on N25: 15A*120V = 1800W
Note on N26: 6A * 120V = 720W
Note on B27: CEC 220.82(C)(1)
Note on N27: 10A*120V=1200W
Note on B28: CEC 220.80(C)(3) 100% of heat pump + 65% of supplemental heating
Note on N28: 15A*120V = 1800W
Note on B29: CEC 220.80(C)(4)&CEC 220.80(C)(5) 65% of total wattage if <4 40% of total wattage if >=4

## Main+ADU Sample
LOAD CALCULATIONS - ALTERNATIVE METHOD PER CEC 220.82 | [6 empty] | VA (Watts) |  | Example Appliances: | Check Manufacturer Specifications for Accurate Power Usage
General Lighting & Receptacle Loads |  |  | CEC 220.82(B) | [5 empty] | Appliance | Typical Load VA (Watt)
|  |  | ADU + Main House area | [5 empty] | HVAC
1 | General Lighting |  | 2000 | sq.ft. x | 3 | VA = | 6000 |  | Central AC/Heat Pump | 7200 | 1800 | /ton | 4 | tons
Small Appliance & Laundry Loads | [8 empty] | Central Furnace | 1200
2 | 2 small appliance circuits |  | 4 | x | 1500 | VA= | 6000 |  | Air Handler | 1000
3 | Additional small appliance |  | 0 | x | 1500 | VA= | 0
4 | Min. 1 laundry circuit |  | 2 | x | 1500 | VA= | 3000 |  | Water heaters
5 | Dryer |  |  |  |  | 2x5000 | 10000 |  | Gas - Tank or Tankless | 0
| Range |  |  |  |  | 2x12000 | 24000 |  | Electric
| Cooktop | [5 empty] | 0 |  | --Tank (Heat Pump) | 4500
| Oven | [5 empty] | 0 |  | --Tankless | Check Product Specifications
| Water Heater |  |  |  |  | 2x4500 | 9000
| Refrigerator |  |  |  |  | 2x1800 | 3600 |  | Laundry
| Dishwasher |  |  |  |  | 2x1200 | 2400 |  | Electric Clothes Dryer | 5000
| Disposal |  |  |  |  | 2x720 | 1440
| Microwave |  |  |  |  | 2x1800 | 3600 |  | Kitchen
| EV Charger |  |  | 0 | x1.25 | = | 0 |  | Electric Cooktop | 10800
| Misc | [5 empty] | 0 |  | Electric Single Oven | 4800
| Subtotal | [5 empty] | 69040 |  | Electric Double Oven | 9000
6 | First 10000 VA @ 100% | [5 empty] | 10000 |  | Electric Range | 12000
7 | Balance @ 40% | Balance=(Row 5- Row 6)= |  |  | 59040 | x0.4= | 23616 |  | Built-in Microwave | 1800
| Subtotal | [5 empty] | 33616 |  | Refridgerator | 1800
Special Appliance Loads | [8 empty] | Disposal | 720
8 | AC/Heating @ 100% | CEC |  |  |  |  | 3600 |  | Dishwasher | 1200
9 | Heat pump + Supplemental Electrical Heating |  |  |  | 0 | x0.65 | 0 |  | Trash Compactor | 1800
| Total | [5 empty] | 37216
EV Charger
| TOTAL LOAD= | [5 empty] | 37216 | VA | 50 Amp | 12000
| Service AMPS = TOTAL LOAD/ 240 V | [5 empty] | 155.0667 | Amps | 40 Amp | 9600
| Minimum Panel Size (75°C terminals) | [5 empty] | 175 | Amps
| Feeder Conductor Size |  |  |  | Copper |  | 1/0 | AWG
| Grounding Size |  |  |  | Copper |  | 0 | AWG | Feeder/Service Conductor Sizing (CEC Table 310.12) |  |  |  | Grounding Electrode (CEC Table 250.66)
[9 empty] | Service/Feeder Rating | Conductor Size (AWG or kcmil)
[10 empty] | Copper | Alu or Cu-Clad Alu |  | Copper | Alu or Cu-Clad Alu
[9 empty] | 100 | 4 | 2 |  | 8 | 6
[9 empty] | 110 | 3 | 1
[9 empty] | 125 | 2 | 1/0
[9 empty] | 150 | 1 | 2/0 |  | 6 | 4
[9 empty] | 175 | 1/0 | 3/0
[9 empty] | 200 | 2/0 | 4/0 |  | 4 | 2
[9 empty] | 225 | 3/0 | 250
[9 empty] | 250 | 4/0 | 300 |  | 2 | 1/0
[9 empty] | 300 | 250 | 350
[9 empty] | 350 | 350 | 500
[9 empty] | 400 | 400 | 600 |  | 1/0 | 3/0
Note on P6: 1 ton = 12k BTU 2-4 rooms - 3 tons typ. 1.5 tons minimum
Note on N20: 45A*240V = 10800
Note on N21: 20A * 240V = 4800
Note on B23: CEC 220.80(B)
Note on N23: 50A x 240V = 12,000VA
Note on N24: 15Ax120V = 1800 max
Note on N25: 15A*120V = 1800W
Note on N26: 6A * 120V = 720W
Note on N27: 10A*120V=1200W
Note on B28: CEC 220.80(C)(3) 100% of heat pump + 65% of supplemental heating
Note on N28: 15A*120V = 1800W