## Electric Appliance Checklist
Electric Panel Size Check
Applicant Name:
Applicant Email or Phone Number:
Site Address:
Date: | 2025-10-14
For Single Family Residence Only |  |  | Instructions:
Approximate Square Footage |  | Sq Ft | 1. Enter the square footage of your house, excluding the garage.
Appliances Proposed/Installed
HVAC
Electric Heat Pump |  |  | 2. Enter Yes if the appliance is electric. Leave bank if it is not electric.
Gas Central Furnace
Electric Wall Heater
Water heaters
Heat Pump Water Heater
Tankless Electric Water Heater
Tank Electric Water Heater
Laundry
Electric Clothes Dryer
Kitchen
Electric Cooktop
Electric Oven (Single)
Electric Range (Cooktop + Oven Combo)
Others
EV Charger
Other Electrical Equipment
Pool Pump
Electric Pool Heater
Is 100A enough? | See Below
Minimum Upgrade:
Please fill in your name, contact info, and address. |  |  | Electrical Load Calculation Spreadsheet
I acknowledge that the information provided is accurate and truthful to the best of my knowledge. |  |  | Type your name
Disclaimer: This is an estimation based on typical single family homes. Load calculations per California Electrical Code may be provided to justify the existing electrical panel capacity.
Clear Appliances

## Background Calculation (hidden)
LOAD CALCULATIONS - ALTERNATIVE METHOD PER CEC 220.82 | [6 empty] | VA (Watts) |  | Example Appliances: | Check Manufacturer Specifications for Accurate Power Usage
General Lighting & Receptacle Loads |  |  | CEC 220.82(B) | [5 empty] | Appliance | Typical Load VA (Watt) | [5 empty] | Heat Pump Table |  | Qty Table
[9 empty] | HVAC | [6 empty] | Sq Ft | Tons
1 | General Lighting |  | 0 | sq.ft. x | 3 | VA = | 0 |  | Central AC/Heat Pump | 2700 | 1800 | /ton | 1.5 | tons | FALSE | 1000 | 1.5 | Yes
Small Appliance & Laundry Loads | [8 empty] | Central Furnace | 1200 |  |  |  |  | FALSE | 1500 | 2
2 | 2 small appliance circuits |  | 2 | x | 1500 | VA= | 3000 |  | Air Handler | 1000 | [5 empty] | 2000 | 3
3 | Additional small appliance |  | 0 | x | 1500 | VA= | 0 |  | Wall Heater | [5 empty] | FALSE | 2500 | 4
4 | Min. 1 laundry circuit |  | 1 | x | 1500 | VA= | 1500 | [8 empty] | 3000 | 5
5 | Dryer | [5 empty] | 0 |  | Water heaters
| Range | [5 empty] | 0 |  | Gas - Tank or Tankless | 0
| Cooktop | [5 empty] | 0 |  | Electric
| Oven | [5 empty] | 0 |  | --Tank (Heat Pump) | 4500 |  |  |  |  | FALSE | Acknowledgement
| Water Heater | [5 empty] | 0 |  | --Tank (Electric Resistance) | 4500 |  |  |  |  | FALSE | FALSE
| Dishwasher | [5 empty] | 1200 |  | --Tankless | Check Product Specifications |  |  |  |  | FALSE
| Disposal | [5 empty] | 720 | [8 empty] | Error Message Table: |  | 0
| Microwave | [5 empty] | 1800 |  | Laundry | [6 empty] | 0 | Please fill in your name, contact info, and address.
| Refridgerator | [5 empty] | 1800 |  | Electric Clothes Dryer | 5000 |  |  |  |  | FALSE | 1 | Please fill in the square footage of your residence excluding the garage.
| Washer | [5 empty] | 1000 | [8 empty] | 5 | Items selected are outside the scope of this check. Please submit electric load calculations for plan review.
| Pool Motor | [5 empty] | 0 |  | Kitchen | [6 empty] | 5 | EV charger, electric tankless water heater, or electric heating equipment selected. Please submit electric load calculations for plan review.
| Subtotal | [5 empty] | 11020 |  | Electric Cooktop | 10800 |  |  |  |  | FALSE | 4 | Please check the acknowlegement below.
6 | First 10000 VA @ 100% | [5 empty] | 10000 |  | Electric Single Oven | 4800 |  |  |  |  | FALSE | 4
7 | Balance @ 40% | Balance=(Row 5- Row 6)= |  |  | 1020 | x0.4= | 408 |  | Electric Double Oven | 9000
| Subtotal | [5 empty] | 10408 |  | Electric Range | 12000 |  |  |  |  | FALSE
Special Appliance Loads | [8 empty] | Built-in Microwave | 1800
8 | AC/Heating @ 100% | CEC |  |  |  |  | 2200 |  | Refridgerator | 1800
9 | Heat pump + Supplemental Electrical Heating |  |  |  | 0 | x0.65 | 0 |  | Disposal | 720
| Total | [5 empty] | 12608 |  | Dishwasher | 1200
[9 empty] | Trash Compactor | 1800
| TOTAL LOAD= | [5 empty] | 12608 | VA
| Service AMPS = TOTAL LOAD/ 240 V | [5 empty] | 52.5333 | Amps | EV Charger
| Minimum Panel Size (75°C terminals) | [5 empty] | 100 | Amps | 50 Amp | 12000
| Feeder Conductor Size |  |  |  |  | Copper | 4 | AWG | 40 Amp | 9600 |  |  |  |  | FALSE
| Grounding Size |  |  |  |  | Copper | 8 | AWG
[9 empty] | Pool Motor | 2400 | 125% | 3000 |  |  | FALSE
[9 empty] | Others | [5 empty] | FALSE
[9 empty] | Pool Heater | [5 empty] | FALSE
[9 empty] | Feeder/Service Conductor Sizing (CEC Table 310.12) |  |  |  | Grounding Electrode (CEC Table 250.66)
[9 empty] | Service/Feeder Rating | Conductor Size (AWG or kcmil)
[10 empty] | Copper | Alu or Cu-Clad Alu |  | Copper | Alu or Cu-Clad Alu
[9 empty] | 100 | 4 | 2 |  | 8 | 6
[9 empty] | 110 | 3 | 1
[9 empty] | 125 | 2 | 1/0
[9 empty] | 150 | 1 | 2/0 |  | 6 | 4
[9 empty] | 175 | 1/0 | 3/0
[9 empty] | 200 | 2/0 | 4/0 |  | 4 | 2
[9 empty] | 225 | 3/0 | 250
[9 empty] | 250 | 4/0 | 300 |  | 2 | 1/0
[9 empty] | 300 | 250 | 350
[9 empty] | 350 | 350 | 500
[9 empty] | 400 | 400 | 600 |  | 1/0 | 3/0
Note on P6: 1 ton = 12k BTU 2-4 rooms - 3 tons typ. 1.5 tons minimum
Note on N22: 45A*240V = 10800
Note on B23: CEC 220.80(B)
Note on N23: 20A * 240V = 4800
Note on N25: 50A x 240V = 12,000VA
Note on N26: 15Ax120V = 1800 max
Note on N27: 15A*120V = 1800W
Note on B28: CEC 220.80(C)(3) 100% of heat pump + 65% of supplemental heating
Note on N28: 6A * 120V = 720W
Note on N29: 10A*120V=1200W
Note on N30: 15A*120V = 1800W